## Slide 1: Source Water Protection Programs Update
Informational Item
Technical Committee
February 7-8, 2018

## Slide 2: Outline – SWP Update
Ohio River Contaminant Source Inventory Pilot Project
Next ODS Renovation
Overview of Spill Response Activities

## Slide 3: Ohio River Contaminant Source Inventory
An Ohio River potential contaminant source inventory would be extremely valuable for source water protection planning and emergency response preparedness.
DRINKING WATER UTILITIES - Develop contaminant source inventories as part of source water protection plans
  Identify potential threats
  Develop contingency plans
EMERGENCY RESPONSE AGENCIES- On parallel path to develop tools to identify sources and aid in spill response planning
  Response tactics
  Anticipate potential impacts

## Slide 4: Contaminant Source Inventory Pilot Project
Initial Study Area – Maysville, KY to Cincinnati, OH
Project Funding - $130,000
  US EPA, GCWW, NKWD
Implement WaterSuite’s Source Water Protection module to assess & manage source water quality risks
  Cloud-based GIS platform
  Pulls contaminant data from existing databases
Maintain data in a shared system
Facilitate emergency response with quick access to information

## Slide 5
Scope & Timeline
Month: | 1 | 2 | 3 | 4 | 5 | 6 | 7-18
1. Project & user set-up |  |  |  |  |  |  | 
2. GCWW data integration |  |  |  |  |  |  | 
3. Create new, editable data layers |  |  |  |  |  |  | 
4. Load additional layers |  |  |  |  |  |  | 
5. Site creation & QA |  |  |  |  |  |  | 
6. Chemical storage data integration |  |  |  |  |  |  | 
7. Chemical research |  |  |  |  |  |  | 
8. Upstream data analytics |  |  |  |  |  |  | 
9. Meeting, training & reporting |  |  |  |  |  |  | 
10. WaterSuite license |  |  |  |  |  |  | 

## Slide 6: Next ODS Renovation
Time to begin planning for next ODS renovation
  Previous renovation began in 2009
Water Users Advisory Committee established a work group
  LWC, GCWW, NKWD, WVAWC, ORSANCO staff
Work Group Objectives:
  Evaluate potential contaminants of concern
  Evaluate new technology applications
  Consider monitoring design options to optimize system
  Provide recommendations to the Commission
Staff is exploring possible funding opportunities for ODS equipment replacement

## Slide 7: Overview of Spill Events
Several noteworthy incidents in the past year
  Mar 02 – Natural Gas Condensate Barges (Racine L&D)
  Oct 21 – Industrial Warehouse Fire (Parkersburg, WV)
  Dec 19 – Urea Ammonia Nitrate Barge Incident (Cincinnati, OH)
  Jan 04 – Barge Grounding (Paducah, KY)
  Jan 10 – M/V Gate City partially sunken tow (Big Sandy River)
  Jan 13 – Barges Gone Rogue (Emsworth L&D & Moundsville, WV)

## Slide 8: Racine Barge Incident Summary
Mar 2 - Tow with 3 barges stuck on Racine Dam
  >3 million gallons of natural gas condensate onboard
Utilities from Huntington to Louisville notified
Tow passed through dam gate
Barges safely recovered
No materials released from barges or tow
Potential to be largest spill since Ashland oil spill in 1988.
  Significant concern for water utilities

## Slide 9: Parkersburg Fire – Early Issues
Notifications
  Local fire crews responded to the fire at 00:30 on Oct 21
  Not reported to NRC until 16:02
  NRC report – air release; no waterways impacted
  OEPA provided updates throughout incident
Firefighting Runoff
  Site along the banks of the Little Kanawha River
  Fire burned for nearly a week
  Firefighting runoff (water and foam) draining directly into river
  Milky white runoff completely miscible; no containment
Unknown Chemicals On-site
  Fire destroyed records of materials stored on-site
Lack of Early Water Quality Sampling
  First WQ samples collected and analyzed on Day 4

## Slide 10: Parkersburg Fire – Water Quality Monitoring
Unknown type and volume of contaminants in runoff
  Site runoff
  Potential contaminants in firefighting foam
Day 4 – First WQ samples collected and analyzed
  Collected from stormwater outfall
  Split samples: 1) contract lab analysis and 2) GCWW
  VOCs, SVOCs, metals
  PFOS/PFOA (contract lab only)
Day 7 – ORSANCO conducted longitudinal survey
  Kanawha River to R.C. Byrd Locks & Dam (~100 miles)
  Split samples again with contract lab and GCWW/WV American
  No detections in Ohio River samples

## Slide 11: Parkersburg Fire – Water Quality Monitoring
Parkersburg ODS was down due to instrumentation failure
WV American ran samples collected by Chemours
  No detections
ORSANCO spill model used to project arrival times
  Slow stream velocities  Required multiple runs to reach downstream utilities
Quick turn-around on screening method samples very helpful to utilities in making treatment decisions
Downstream ODS sites increased sampling frequency and utilities made treatment adjustments
No Ohio River detections noted

## Slide 12: UAN Barge Incident – Initial Report
Notification – December 19 (8:51)
  NRC report indicated barge “cracked in half” while offloading (ORM 478.7)
  Urea ammonia nitrate was discharging into the river
  Amount of release initially not reported
ORSANCO received phone notifications from OEPA, KY DEP, USCG
ORSANCO notified Louisville Water Company
  Sent notification via spills distribution list
Time-of-Travel modeling requested by KY DEP, LWC, USCG, Clifty Creek Power Plant

## Slide 13: Initial Water Quality Sampling
RP’s Contractor – CTEH
  Collected WQ samples for certified analysis daily at four locations
    Upstream, at incident location, peak locations, leading edge
    Approached followed daily from 12/19 thru 12/23
ORSANCO / Louisville Water Company
  LWC raised concerns regarding ability to maintain treatment
  Requested assistance to conduct longitudinal field screening
  Longitudinal surveys conducted 12/20 and 12/21
  Peak concentration dropped from 3.1 to 1.4 mg/L
  Sampling confirmed material was vertically well mixed
ORSANCO coordinated daily WQ conference call

## Slide 14: Fixed Station Monitoring
Initial time-of-travel model estimated travel time to Louisville at 9 days (i.e. 12/28)
Precipitation increased river velocities significantly.
  Moved up projected arrival at Louisville by 2.5 days (i.e. mid-day on 12/25)
Transitioned to fixed station monitoring at Markland Locks & Dam
  CTEH sampled overnight from 12/23 to 12/24

## Slide 15: Markland Results
Sampling initially from lock wall; repositioned to hydro side
First detection: 19:45 on 12/23
Collected samples hourly
Peaked near 1 mg/L
Discontinued mid-day on 12/24 to transition equipment to Westport site

## Slide 17: Silver Linings
Significant rain diluted ammonia concentration
Low water demand on Christmas Day allowed LWC intake to be shut down much longer than normally possible
Lots of time-of-travel data to calibrate spill model.
Louisville Water, through proactive treatment management, met all compliance requirements
Evansville also able to provide adequate treatment (peak 0.26 mg/L on 12/29)

## Slide 18: UTV City of Cassville – Barge Grounding
Notified by KY DEP – January 4
  No NRC report (Occurred Jan 3)
Tow with barges pushed into bank to perform maintenance
Pool dropped 2 feet overnight, leaving the barges grounded
13 red flag barges (methanol, acetone, styrene, and others)
Concern barges could be punctured by bottom substrate as pool continued to drop
Incident location 923.5 (12 miles upstream of Paducah Water)
Contingencies planned in the event of a release
Significant coordination by USACE to manage river stage
Barges freed on Sunday January 7

## Slide 19: M/V Gate City Sinking – Initial Report
Notification: NRC January 10 (8:03)
  Received additional notification from OEPA
Partially sunken vessel discharging oil into water
Big Sandy River mile 8
Sheen size 200 feet
Volume released unknown
ORSANCO notified downstream utilities and sent email to spills distribution list

## Slide 20: M/V Gate City – Follow-Up Details
USCG indicates sheen is 3 miles long
Initial report of potential 1,000 gallons diesel on-board
Later updated to 5,000 gallons potentially on-board
Kenova Water shut down prior to sheen reaching intake
Booms deployed at Kenova, Ashland, and Russell intakes
KY DEP initially state lead; control transitioned to WV DEP Jan 11
USCG coordinated daily conference calls

## Slide 21: M/V Gate City - Monitoring
KY DEP established contractor support through Pace
Samples collected daily at 4 locations
  Upstream, at incident, and 2 downstream locations
  Day 1 samples indicated presence of some PAHs in low ppb range
  Levels continued to decrease over time
Ashland ODS – Approximately 10 miles downstream
  Jan 11 – Unidentified VOC peaks
  Jan 12 - Detects for 1,3 dichlorobenzene and 1,4 dichlorobenzene <1 ppb
Portsmouth ODS increased sampling frequency
Maysville ODS – Frozen water line

## Slide 22: M/V Gate City – Kenova Water
Intake shut down on Jan 10
Trucked in water from Huntington and received additional water from Ashland
Much of town without water by Jan 12
Needed WQ sample from intake to reopen
  Snow storm closed labs
  WV American to the rescue – Ran sample from intake late Friday night
  Had low level detects (~1 ppb) for methylene chloride, and too low to quantify for acetone, benzene, and toluene
Intake reopened Jan 13 upon receipt of sampling results and added capability to apply carbon
Feb 3 - Vessel raised and relocated to cleaning facility

## Slide 23: Break-Away Barge Day – January 13
Two separate break-away barge incidents on same day
Notification: NONE (via Facebook and Google)
Emsworth Lock & Dam
  27 barges broke away from moorings at Ohio River mile 4
  7 barges went over Emsworth Dam
  Remaining barges stacked up on face of dam
  Carrying coal and cement powder
Wheeling to Moundsville
  40 barges broke away from moorings at ORM 93
  4 red flag barges; corralled quickly
  5 other barges sank; 1 carrying coal
Incidents caused by high water and ice flows

## Slide 24: Post-Incident Take-Aways
Early collection of WQ samples critical to characterize the location and magnitude of release (eliminate unknowns)
Split samples for certified and screening analyses extremely helpful to get results quickly to inform treatment decisions
  Longitudinal field screening pinpoints leading edge and peak concentrations
Reinforced value of collaborative network of ODS partners to assist fellow utilities (analytical services and treatment guidance)
Emphasized importance of engaging state drinking water agencies early in response
Identified spill model limitations (limited range during low flow)
Spill model performed well during UAN spill
Need to rectify disconnect between NRC and 911 notifications