## Slide 1: Fine-mesh Screens: Entrainment BTA
www.asaac.com
Rob Reash – American Electric Power ORSANCO Technical Committee Meeting 4 June 2019

## Slide 2: Historical Perspectives
1972 Clean Water Act Amendments
  100% mortality assumed
  Ignore/unaware Kerr (1953) & Markowski (1962)
1980 – Hudson River Settlement Agreement
  USEPA consultants acknowledge survival
    Utility-sponsored studies
    ORNL simulator studies
2004 Phase II Rule
  USEPA reverted to 100% mortality default
  May perform site-specific study (benefits)
2014 New 316(b) rule
  Acknowledge importance of survival

## Slide 3: Entrainment BTA
§122.21(r)(11) Benefits Valuation Study
All existing facilities that withdraw greater than 125 mgd AIF and others as directed must develop for submission to the Director an evaluation of the benefits of the candidate entrainment reduction technologies and operational measures evaluated in §122.21(r)(10)
Baseline: Reflects conditions without alternative
= No Action Alternative
Benefit : Difference in economic welfare to humans over that would exist without change
= Economic value of reductions in entrainment
Solutions through Science

## Slide 4: Entrainment Survival and the 2014 316(b) Rule
Comment Responses -With regard to entrainment survival, EPA does allow for consideration of entrainment survival. ……. mortality after passing the cooling water intake structure must be counted as 100 percent mortality unless you have demonstrated to the approval of the Director that the mortality for each species is less than 100 percent.
§122.21 (r) (7) Entrainment Performance Studies. The owner or operator of an existing facility must submit any previously conducted studies or studies obtained from other facilities addressing technology efficacy, through-facility entrainment survival, and other entrainment studies…… Any studies conducted at other locations must include an explanation as to why the data from other locations are relevant and representative of conditions at your facility. In the case of studies more than 10 years old, the applicant must explain why the data are still relevant and representative ……..

## Slide 5: Entrainment Survival and BTA
§125.94 (d) BTA standards for entrainment for existing facilities. The Director must establish BTA standards for entrainment for each intake on a site-specific basis. These standards must reflect the Director’s determination of the maximum reduction in entrainment warranted after consideration of the relevant factors as specified in § 125.98.
§125.98 (f) (2) The proposed determination in the fact sheet or statement of basis must be based on:
  (v) Quantified and qualitative social benefits and costs of available entrainment technologies.
(3) The proposed determination in the fact sheet or statement of basis may be based on:
  (i) Entrainment impacts on the waterbody;

## Slide 6: Benefits Valuation: Four Step Process
Solutions through Science
Estimate Annual Entrainment and Impingement Reduction
Convert Losses to Effects on Resources of Interest
Estimate Annual Benefit of Resource Effects
Estimate Total Benefit Over Facility Lifetime
Biology
Economics
Notes: Important that r6 and r11 coordinate to avoid Impingement issues.

## Slide 7: Entrainment Technologies
Closed-cycle cooling
Fine-mesh screens
  Mesh size of 2 mm or smaller
Reuse of water or alternate sources of cooling water
Other technologies identified by the applicant or requested by the Director.
Solutions through Science

## Slide 8: Fine-Mesh Screens
Traveling Screens
  Overlays on existing screens
  New modified screens
Narrow-slot cylindrical wedgewire screens
  Not focus of this presentation
Solutions through Science
Source: EPRI 2003
Notes: If existing screens are conventional without fish protection features, then additional modifications will be necessary. Cost will approach new screens. Fish return system consideration.
Velocities will increase. May need to consider expansion of the intake to maintain lower velocities.
WWS are designed to maintain 0.5 fps so impingement compliant as well.

## Slide 9: Critical Benefits Assumptions
Survival
  Excluded – EPA assumes 100% survival
  Through plant - EPA assumes 0% survival
O&M Costs
  Consequence of screen outages or failures = $$$
  Continuous rotation
Solutions through Science

## Slide 10: Factors Impacting Fine-Mesh Screen Survival
Mesh size
Rotation speed (duration of impingement)
Through-screen velocity
Organism size (>12 mm)
Impacts of debris loading
Characteristics of the wash, handling, and return systems
Solutions through Science
Notes: Spray wash pressure, transit time, return location, predation risk

## Slide 11: Results of Research To Date
Survival is species/lifestage specific
Lower through-screen velocities are more conducive to survival but no definitive threshold
Reduced impingement duration improves survival
Larger organisms survival better
There is a tradeoff between survival of larvae impinged on fine-mesh and through plant survival
Solutions through Science

## Slide 12: Case Studies
Two EPRI projects have examined survival of entrainable size organism excluded by fine-mesh screens
  Field studies
  Traveling screens with 0.6 mm fine mesh overlays
  Simultaneous sampling at three locations allowed comparison of exclusion and through plant survival
Solutions through Science

## Slide 13: ConEd East River Station
Solutions through Science
Water intake - 369 MGD
Once through cooling
5 dual flow screens
TSV – 1 ft/sec with 3/8” mesh, slightly higher at screen outfitted with fine mesh
Delta T ~ 3 degrees avg.
SPDES permit requirement to use 0.6 mm fine-mesh overlays seasonally.

## Slide 14: ConEd East River Station
Solutions through Science
Taxon | Stage | Entrainment Survival Estimate (%) | Exclusion Survival Estimate (%)
Cunner | Egg | 99.4 | 61.3
Tautog | Egg | 93.8 | 73.1
Labridae | Egg | 98.8 | 66.2
Bay Anchovy | Egg | 100.0 | 52.6
Oth fish eggs | Egg | 99.0 | 93.7
Unid eggs | Egg | 86.7 | 46.1
Atlantic Silverside | Larvae | 78.1 | -
Naked Goby | Larvae | 58.4 | -

## Slide 15: Permitting Consequence
Solutions through Science
Seasonal Use of Fine-Mesh Screens No Longer Required at ERGS!

## Slide 16: DTE Monroe Power Plant
Solutions through Science
Electric – 3,080 MW
Water intake – 2,056 MGD
Once through cooling
Skimmer wall extending to 14ft from bottom
16 vertical traveling screens with 3/8” mesh
TSV – 1.6 ft/sec
Delta T ~12 degrees
Proactive approach to study, no permit requirement or BTA determination. Data to inform benefits valuation.

## Slide 17: DTE Monroe Power Plant
Solutions through Science
Taxon | Stage | Entrainment Survival Estimate (%) | Exclusion Survival Estimate (%)
Freshwater drum | Eggs | 73.6 | 97.1
Unidentified | Eggs | 37.4 | 100.0
Alewife | Larvae | 17.3 | 0
Clupeidae | Larvae | 30.3 | 0
Freshwater drum | Larvae | 34.4 | 0
Gizzard shad | Larvae | 30.2 | 0
Moronidae | Larvae | 35.5 | 0.1
Percidae | Larvae | 10.1 | 0.2
Shad/Smelt/Alewife | Larvae | 16.8 | 0
Unidentified | Larvae | 10.0 | 0

## Slide 18: Permitting Consequence
Solutions through Science
To be determined
Results suggest that fine mesh panels were not effective
Site-specific study data incorporated into the benefits valuation study

## Slide 19: Conclusions
Solutions through Science
Accounting for through plant survival may reduce risk of a fine-mesh screen BTA determination.
Fine-mesh screen survival is not 100%. Assuming otherwise biases BTA toward fine-mesh screens.
Reference through plant and fine-mesh screen survival studies that have been conducted.
Demonstration study post-BTA determination is an option and may not require full retrofit to fine-mesh.