## Slide 1: Source Water Protection & Spill Response Update
ORSANCO Technical Committee
October 8-9, 2019
Informational Item

## Slide 2: Program Elements
Harmful Algal Blooms
  New monitoring stations
Spill Response
  Overview / Update
Source Water Protection Planning
  Contaminant Source Inventory Project
Organic Detection System (ODS)
  ODS Next Generation – Next Steps

## Slide 3: Spill Response
Communication
  Initial Notifications (24/7)
  Facilitate/coordinate communication and actions
  Cincinnati Focus Group meeting Sept 24
Time-of-Travel Modeling
  US EPA funding fixes to model
  Current IT issue in receiving flow files
Water Quality Monitoring
  Some recent events required notifications, but none required field response by ORSANCO
Analytical Support
  Utilize ODS sites to run samples to track spill

## Slide 4: Source Water Protection Planning

## Slide 5: Contaminant Source Inventory Project
Objective: Develop GIS database tool to assist water utilities in assessing potential water quality risks.
Utilizes WaterSuite software to map contaminant threats and associated information
US EPA, Greater Cincinnati Water Works, & Northern Kentucky Water District

## Slide 6: Contaminant Source Inventory Project
Phase 1 – Maysville to Cincinnati
  Initial mapping completed Fall 2018
Phase 2 –
  Extend study area to upstream of Portsmouth, OH
  Evaluate source water protection and emergency response priorities
  Update Tier II data
Maysville and Portsmouth water utilities participating
Time-of-travel model comparison
Next phase to extend area

## Slide 7: ODS Next Generation Next Steps

## Slide 8: Volatile Organics Monitoring Network
Notes: Our network is currently comprised of 17 active monitoring stations: by Instrumentation we have 9 GCMS, 3 GC(FID) 5 GC(AID) (on-line process GC’s). Our newest site, on the Elk River, near Charleston became active in Fall 2017.

## Slide 9: Value of System
Serves as a sentinel to alert water utilities
Examples
1994 – EDB from Shell Chemical fire
2009 – Unreported methylene chloride release
2014 – MCHM release in Charleston, WV
2017 – Parkersburg warehouse fire
Quick turn-around screening provides water utilities with key information to make informed management decisions to protect consumers

## Slide 10: ODS Next Generation
Previous renovation initiated in 2009
Work Group Participants
  American Water Company
  Greater Cincinnati Water Works
  Louisville Water Company
  Northern Kentucky Water District
  US EPA
  ORSANCO
Work Group Charge –
  Evaluate potential contaminants of concern.
  Evaluate available technologies
  Identify at least 3 monitoring designs
  Recommend preferred option

## Slide 11
ODS System Configuration Scenarios |  |  |  |  |  |  | 
 |  |  |  | Annualized Cost |  |  | 
# | Description | Instrumentation | Total Capital | Maintenance Labor Hours | Capital Cost* | Maintenance Cost** | Total Annual Cost
1 | Current system + SVOC at 4 sites | 9 GC/MS 3 GC/FID 4 CMS 4 GC/FID (SVOC) 1 Backup CMS | $2,441,000 | 550 | $276,100 | $271,500 | $547,600
2 | Current system | 9 GC/MS 3 GC/FID 4 CMS 1 Backup CMS | $2,121,000 | 438 | $212,100 | $207,500 | $419,600
3 | Replace 3 GC/MS with GC/FID | 6 GC/MS 6 GC/FID 4 CMS 1 Backup CMS | $2,013,000 | 390 | $201,300 | $187,000 | $388,300
4 | Replace 5 GC/MS with 3 GC/FID & 2 CMS | 4 GC/MS 6 GC/FID 6 CMS 1 Backup CMS | $1,803,000 | 394 | $180,300 | $169,400 | $349,700
* Annualized capital cost assumes 10-year replacement schedule. |  |  |  |  |  |  | 
** Annualized maintenance cost excludes staff labor and travel expenses. |  |  |  |  |  |  | 

## Slide 12: Summary of Recommendations
Maintain VOCs as primary focus for routine monitoring system.
Expand calibrated suite of VOC analytes for routine analysis.
Scoring matrix developed can be used to prioritize placement of GC/MS instruments.

## Slide 13: Summary of Recommendations
Trial SVOC analysis at 2-3 sites with existing equipment to evaluate cost and time implications
Evaluate possible web-portal for utilities to share routinely-collected water quality results
Continue ODS Next Gen Work Group to guide ongoing recommendations.

## Slide 14: Summary of Recommendations
The three GC instrument system types currently employed remain the preferred instrument choices.
Four configuration options presented provides decision tool to optimize system to available resources.
Network with 5 GC/MS units considered minimum required to meet routine and spill response monitoring needs.
Maintaining current system configuration deemed preferred option.

## Slide 15: Next Steps
Evaluate expanded VOC analyte list
  Developed candidate list of 10 VOCs
  Determine which ones are practical with current system instruments and methods
Test semi-VOC analysis at 2 or 3 sites
  Evaluate costs of adding SVOCs
  $$$ and time
Evaluate development of data sharing web-portal among water utilities
ODS Next Gen Workgroup will meet to discuss details of next steps

## Slide 16: Questions?