## Slide 1: Markland Hydropower Water Quality Monitoring Plan
Technical Committee Meeting
October 4-5, 2016
Agenda Item XX

## Slide 2: Background
Duke Energy – Owner & operator of the Markland hydropower generating facility
FERC relicensing process required:
  Installation of continuous WQ monitors
  Complete 5-Year dissolved oxygen (DO) study
  Submit DO monitoring & compliance plan to IDEM
  License requires consultation with IDEM, ORSANCO, and USACE Louisville District prior to submitting final plan to IDEM for approval.

## Slide 3: Markland WQ Monitoring Plan
Draft monitoring plan submitted in late May
Duke presented results of the 5-Year WQ study and the draft monitoring plan at June Technical Committee meeting.
ORSANCO staff has reviewed the plan for consistency with Commission’s policy on WQ monitoring at hydropower facilities

## Slide 4: Purpose of Presentation
Present staff’s review and recommendations on the draft WQ monitoring and compliance plan.
Receive direction from the Technical Committee regarding submission of comments to IDEM on the draft plan.

## Slide 5: Overarching Considerations
IDEM holds ultimate authority of approval for the Markland WQ Monitoring & Compliance Plan
Hydropower project licenses typically last for 50 years.
Several new Ohio River hydropower projects are in the pipeline for development.

## Slide 6: ORSANCO Hydropower Policy
“Operating licenses for Ohio River hydropower facilities should contain provisions to assure that:”
Studies conducted to define aeration characteristics of the dam.
Collect DO data above and below facility; make data remotely available to ORSANCO.
Design and operate to maintain full aeration potential of the dam during critical conditions.

## Slide 7: Compliance Plan and Schedule Elements
Continuous DO / temp monitoring (USGS)
Provision for independent accuracy checks of USGS instrumentation
WQ triggers for hydro operation curtailment
  < 5 mg/L (daily average); < 4 mg/L (instantaneous) triggers
  Potential for future turbine aeration removing triggers
  Provisions for electric grid emergencies
  Provision for persistent degraded water quality episodes

## Slide 8: 1. Continuous Monitoring
Duke Proposal:
  Maintain 2 DO/temp sensors (USGS)
  Deployed June 1 – October 31
  Data available via web
Key Considerations:
  Policy is silent on period of deployment
  DO criteria for critical spawning season Apr 15-Jun 15
Staff Recommendation:
  Deploy sensors from April 15 thru October 31

## Slide 9: 2. Independent Accuracy Checks
Duke Proposal:
  Right to conduct independent accuracy checks of sensors
Key Considerations:
  DO sensors are known to experience calibration drift
  USGS response time is one to two days
Staff Recommendation:
  No change recommended

## Slide 10: WQ Triggers to Suspend Generation Scenario #1 – Existing Turbines
Duke Proposal (assumes existing turbine status):
  Suspend generation if :
    One-third of 15 minute readings are below 5.0 mg/L; or
    Two consecutive readings are below 4.0 mg/L
Key Considerations:
  Policy does not detail compliance metrics.
Staff Recommendation:
  No changes recommended.

## Slide 11: WQ Triggers to Suspend Generation Scenario #2 – Modified Turbines
Duke Proposal (assumes turbines with aeration):
  Eliminate WQ triggers from compliance requirements provided demonstration study confirms new turbine modifications increase DO by 0.2 mg/L or greater.
Key Considerations:
  Study found passing water thru the dam instead of hydro increased DO by 0.3 mg/L to 0.5 mg/L.
  Policy calls for hydro operation to maintain “full aeration potential of dam during critical conditions”.
Staff Recommendation:
  Demonstrate new turbines increase DO by 0.5 mg/L or more.
  Conduct periodic surveys to confirm turbine aeration capacity over life of license.

## Slide 12: WQ Triggers to Suspend Generation Scenario #3 – Energy Emergencies
Duke Proposal:
  Temporarily override WQ triggers during energy demand emergencies.
Key Considerations:
  Policy calls for hydro operation to maintain “full aeration potential of dam during critical conditions”.
  Circumstances for special exemptions are not detailed in policy.
Staff Recommendation:
  Request that applicant clarify situations in which energy emergencies may be declared and by what “applicable authorities.”

## Slide 13: WQ Triggers to Suspend Generation Scenario #4 – Extended Period Events
Duke Proposal:
  Temporarily suspend WQ triggers during unusual, persistent adverse water quality events.
    2015 HAB given as an example persistent adverse WQ event
Key Considerations:
  Policy calls for hydro operation to maintain “full aeration potential of dam during critical conditions”.
  Circumstances for special exemptions are not detailed in policy.
Staff Recommendation:
  Remove provision from plan and maintain WQ triggers in effect during extended low DO periods.

## Slide 14: Summary of Staff Recommendations
  Deploy sensors from April 15 thru October 31.
  No changes recommended to request to conduct independent accuracy checks.
  No changes recommended to proposed compliance metrics.
  Demonstrate proposed turbine modifications increase DO by 0.5 mg/L or more; and, Conduct periodic surveys to confirm turbine aeration capacity over life of license.
  Request applicant clarify situations in which energy emergencies may be declared and by what “applicable authorities.”
  Remove provision from plan and maintain WQ triggers in effect during extended low DO periods.

## Slide 15: Committee Discussion
Direction to staff on submission of comments to IDEM on the Markland Water Quality Monitoring and Compliance Plan